WEEKLY OPERATIONS REPORT

1. **DOCUMENT ID#: CPI-OPS-7601-191104-AM1**
2. **TITLE: TAYLOR COGEN GONZALES WEEKLY OPERATIONS REPORT**
3. **START DATE: 11/04/19**
4. **END DATE: 11/10/19**
5. **KEY METRICS:**

Cogen Production: 196,520 kWh

% of Gross Load Served: 54.5%

Net Grid After All Generation: 164,251 kWh

Net Exports: 22,289 kWh

Cogen Run-hours: 115.00 run-hours

1. **UNPLANNED OUTAGES:** 1. Genset tripped offline Monday at 10:43 A.M. during update to voltage regulator settings. Downtime: 10 minutes. Voltage regulator found to be cause of previous week’s outages.

2. Genset taken offline Wednesday at 5:36 A.M. for 2,000-hour scheduled maintenance, during which time a front-end engine oil leak was repaired, and updates to relay settings were addressed. Downtime: 52 hours, 15 minutes.

1. **OPERATING NOTES:** 1. Facility load data not gathered during relay settings update from Wednesday at 11:36 A.M. to Thursday at 11:21 A.M.

2. Genset programed to run at 1850 kW with load following.

1. **UPCOMING:** 1. M700 commissioning is delayed due to maintenance.